FESTO CP FACTORY SMART MAINTENANCE

Master OPC UA Node, Sensor Telemetry & Data Label Reference Guide
German Jordanian University (GJU) Smart Factory Laboratory

This reference document provides a complete mapping of network server endpoints, continuous telemetry channels, OPC UA discrete PLC address space tags, and standardized data labels for AI model training on the Festo CP Factory.

# 1. Network Server Endpoints & Station IP Map

| Workstation / Layer | PLC / Gateway Type | OPC UA Endpoint IP URL | Function / Scope |
| --- | --- | --- | --- |
| Station 1 (ASRS) | Siemens S7-1500 PLC | opc.tcp://172.21.1.1:4840 | Warehouse Storage & Retrieval |
| Station 2 (Linear) | Siemens S7-1500 PLC | opc.tcp://172.21.2.1:4840 (or .7.1) | Linear Branching Conveyor |
| Station 3 (RASS PLC) | Siemens S7-1500 PLC | opc.tcp://172.21.3.1:4840 | Mitsubishi RV-4FL Robot PLC |
| Station 3 (RASS Energy) | Festo CPX-E_EMB_RASS | opc.tcp://172.21.3.60:4840 | RASS Robot Local Power & Air |
| Station 4 (Magazine) | Siemens S7-1500 PLC | opc.tcp://172.21.4.1:4840 | Workpiece Magazine Feeding |
| Station 5 (Muscle Press) | Siemens S7-1500 PLC | opc.tcp://172.21.5.1:4840 | Pneumatic Muscle Press PLC |
| Station 5 (Press Energy) | Festo CPX-E_EMB_MPRESS | opc.tcp://172.21.5.60:4840 | Muscle Press Local Power & Air |
| Central Line Energy | Festo CPX-E_Energy | opc.tcp://172.21.0.60:4840 | Total CP Line Power & Air Header |
| Central MES4 Server | Festo Ciros Studio / MES | opc.tcp://172.21.0.90:4840 | Central MES Production Server |

# 2. Continuous 33-Sensor Telemetry Channels (MES4 / CPX-IOT Stream)

| Sensor Channel Name | Unit | Measurement Scope | AI Maintenance Significance |
| --- | --- | --- | --- |
| Pressure | bar | Pneumatic Line Air Pressure | Detects leaks, pressure drops & FRL regulator issues |
| Flow | L/min | Active Moving Air Volume Rate | Detects cylinder actuation spikes & line blowouts |
| ActivePowerTotal | Watts (W) | Total 3-Phase Electrical Power | Primary indicator of total mechanical workload & speed |
| ActivePowerL1 / L2 / L3 | Watts (W) | Per-Phase Electrical Power Distribution | Detects phase unbalance & single-phase overload |
| CurrentL1 / L2 / L3 | Amperes (A) | 3-Phase Line Currents | Detects motor friction, mechanical binding & load shifts |
| VoltageL1 / L2 / L3 | Volts (V) | 3-Phase AC Line Voltages | Monitors supply voltage stability & brownouts |
| PowerFactorL1 / L2 / L3 | Ratio (0-1) | Electrical Power Factors per Phase | Indicates inductive motor efficiency & reactive loss |
| ReactivePowerTotal | VAR | Total Reactive Electrical Power | Measures inductive motor magnetizing load |
| ReactivePowerL1/L2/L3 | VAR | Per-Phase Reactive Power | Diagnostic metric for motor winding degradation |

# 3. OPC UA Station PLC Discrete Tag Reference (S7-1500 Address Space)

IEC 61131-3 Naming Rules: x = Boolean (0/1), r = Real (float), MB = Solenoid Valve Command (Magnet-Befehl), GF = Device Feedback (Geräte-Feedback), BG = Limit Switch, Out = Digital Output.

| PLC Tag Name (UaExpert) | Signal Type | Physical Hardware Component | Manual Citation & Page |
| --- | --- | --- | --- |
| xG1_MB20 | BOOL (Output) | Stopper 1 Solenoid Valve Lower/Extend | RASS Manual p.184 / ASRS Manual p.95 |
| xG1_MB21 | BOOL (Output) | Stopper 1 Solenoid Valve Raise/Retract | EPLAN Schematics p.37 |
| xG1_MB30 | BOOL (Output) | Stopper 2 Solenoid Valve Lower/Extend | RASS Manual p.184 / ASRS Manual p.97 |
| xG1_MB40 | BOOL (Output) | Stopper 3 / Bypass Solenoid Valve | RASS Manual p.185 |
| xG1_GF25 | BOOL (Input) | Stopper 1 Device Position Feedback | EPLAN Schematics p.38 |
| xG1_BG20 | BOOL (Input) | Stopper 1 Down Limit Switch | RASS Manual p.184 |
| xG1_BG21..BG24 | BOOL (Input) | Pallet RFID & Optical Identity Sensors | RASS Manual p.184 |
| xG1_Out00 / Out01 | BOOL (Output) | Conveyor Belt Motor Run & Direction Relays | ASRS Manual p.144 |
| xG1_Out02 / Out03 | BOOL (Output) | Station Signal Tower Lamps (Green/Yellow/Red) | RASS Manual p.158 |
| xH_D1 / xH_D2 | BOOL (Handshake) | Station-to-Robot Handshake (Ready to Pick) | RASS Manual p.158 |

# 4. Standardized Failure Mode Data Labels for ML Training

| Dataset Label String | Failure Mode Description | Lab Physical Induction Method | AI Performance Status |
| --- | --- | --- | --- |
| NORMAL | Healthy Baseline Operation | 100% Robot Speed, 6.6 bar supply, 3 carriers | 🟢 100% Real Lab Data |
| FM01_PRESSURE_DROP | Air Supply Pressure Drop / Leakage | FRL Regulator set to 5.0 bar (MS6-LFR) | 🟢 100% Real Lab Data (1.00 F1) |
| FM02_FLOW_RESTRICT | Partial Flow Restriction | Stopper Cylinder Needle Valve 2 turns CW | 🟡 Protocol Ready / Smoke tested |
| FM03_FLOW_HEAVY_RESTRICT | Heavy Flow Restriction (~75%) | Stopper Cylinder Needle Valve 4 turns CW | 🟡 Protocol Ready / Smoke tested |
| FM04_OVERLOAD | Conveyor Belt Slip / Motor Overload | Conveyor belt tension adjustment screw | 🟡 Protocol Ready / Smoke tested |
| FM05_IDLE_NO_LOAD | Empty Station Cycle (No Workpiece) | Cycle executed without pallet in station | 🟡 Protocol Ready / Smoke tested |
| FM06_SPEED_REDUCTION | Robot Speed Override (50%) | Robot controller speed override set to 50% | 🟢 100% Real Lab Data (1.00 F1) |
| FM07_PHASE_IMBALANCE | Electrical Sub-Device Phase Shift | Sub-device load disabled in MES4 | 🟡 Protocol Ready / Smoke tested |
| FM08_SENSOR_OBSTRUCT | Optical Sensor Lens Obstruction | Semi-transparent film over optical lens | 🟡 Protocol Ready / Smoke tested |
| FM09_INTERMITTENT | Dynamic Pressure Modulation | Regulator knob modulated 5.0 ↔ 6.6 bar | 🟡 Protocol Ready / Smoke tested |
| FM10_OVERPRESSURE | Line Overpressure (~7.8 bar) | FRL Regulator set to 7.8 bar | 🟡 Protocol Ready / Smoke tested |